## 00_README
Topik | Keterangan
MANTAPS - Corporate Topology Register
Konsep | Excel = authoring / staging / review topologi relasional. BUKAN tempat menggambar SLD.
Output | Engine membentuk canonical model + generate SVG SLD + hitung Tier + overlay.
Granularitas | Node = GI/GITET/pembangkit. Edge = penghantar/IBT link. Bay/CB = level PLMS/NMM, tidak wajib.
Status | ENERGIZED / NEW_NOT_ENERGIZED / PLANNED / DE_ENERGIZED / OWNED_BY_CUSTOMER (dari warna busbar SLD).
Tier | Dihitung engine per-view dari SOURCE via GI-graph. TIDAK disimpan di GI (satu GI bisa beda Tier per proyeksi).
Multi-SS | Satu GI fisik bisa jadi anggota beberapa subsistem (sheet 06). Objek fisik disimpan sekali.
Round-trip | Import kembali -> ObservedObject/ObservedConnection -> reconciliation -> canonical. Tidak menimpa langsung.

## 01_SUBSTATION
Code | Name | Type | Voltage_kV | APB | UIT | Status | Busbar_Config | Busbar_Note | Has_Transformer | Has_Capacitor | Symbol_Note | Lat | Lon | Asset_ID | Note
ABDGP | Abadi Guna Papan | GIS | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | GIS AGP. Ruas AGP-Mampang SKTT baru 1000A. Feeder Senayan-AGP masih PLANNED.
ALTRA | Alam Sutera | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
BLRJA | Balaraja | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
BSH | BSH | KTT | 150 | UP2B Jakarta & Banten | JBB | OWNED_BY_CUSTOMER | UNKNOWN |  | 1 | 0 |  |  |  |  | Dalam kotak dashed 'Aset milik KTT'
CKBRU | Cikupa Baru | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
CKNDE | Cikande | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | GI batas ke SS Cilegon
CKUPA | Cikupa | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Irisan 2 SLD. Kerawanan #4 (Cikupa-Jatake).
CLDUG | Ciledug | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 1 | 1 shunt capacitor
CNKNG | Cengkareng | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Kerawanan #5 (Durikosambi-Cengkareng)
CURUG | Curug | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
DKSBI | Durikosambi | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | DOUBLE_SECTIONALIZED | Bus 1A / 2A / 1B / 2B | 1 | 0 |  |  |  |  | GI batas; irisan 2 SLD. Kerawanan #5 (Durikosambi-Cengkareng).
DNYSA | Danayasa | GIS | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | DOUBLE_1CB | gap bus section di SLD | 1 | 0 |  |  |  |  | GI batas -> SS Gandul 2,4. Ruas Mampang-AGP-Danayasa. Dialihkan ke SS Cawang 2,3-Depok 1 saat pemeliharaan Kembangan-New Senayan.
GITET_KMBGN | GITET Kembangan | GITET | 500 | UP2B Jakarta & Banten | JBB | ENERGIZED | DOUBLE_1CB |  | 0 | 0 |  |  |  |  | GITET 500 kV, 2x IBT 500/150 ke bus Kembangan 150
GITET_NBRJA | GITET New Balaraja | GITET | 500 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | GITET 500 kV, 2x IBT 500/150 ke bus New Balaraja 150
GJTGL | Gajah Tunggal | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Single phi (kerawanan #3)
ITS | KTT ITS | KTT | 150 | UP2B Jakarta & Banten | JBB | OWNED_BY_CUSTOMER | UNKNOWN |  | 0 | 0 |  |  |  |  | Konsumen tegangan tinggi
JTAKE | Jatake | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 1 | 2 shunt capacitor |  |  |  | Irisan 2 SLD. Kerawanan #4.
JTKBR | Jatake Baru | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Tier 6. Disuplai dari Jatake (sisi Kembangan) / Tangerang (sisi Balaraja). Irisan 2 SLD.
KMBGN | Kembangan | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | DOUBLE_1CB | 2 bus, 1 CB kopel, tanpa section | 0 | 0 |  |  |  |  | Bus 150 kV disuplai IBT-1,2 Kembangan. Kerawanan #1. Ada 1 GI trafo-only tak berlabel di ujung kiri bus (di-skip).
LTKNG | Lontar | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | GI outlet PLTU Lontar (BUKAN GI Teluknaga). Busbar Tier-1 panjang.
MAXIM | Maxim | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 | 3 trafo di SLD (perlu konfirmasi OSL)
MPANG | Mampang | GIS | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | GIS Mampang Baru. Ujung ruas Mampang-AGP-Danayasa.
MTLAN | Metland | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
NBRJA | New Balaraja | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | Bus 150 kV disuplai IBT-1,2 New Balaraja
NCKUPA | GITET New Cikupa | GITET | 500 | UP2B Jakarta & Banten | JBB | NEW_NOT_ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | GITET (IBT 500/150) BELUM energize -- busbar hitam di SLD. Solusi kerawanan #4: dibangun untuk menyuntik daya di titik Cikupa-Jatake agar ruas tidak overload. Saat COD nanti = perubahan struktural (TopologyVersion baru, kemungkinan SS baru) via change request -- BUKAN toggle. Node disimpan sbg informasi; tidak dihitung dalam Tier kondisi sekarang.
NSYAN | New Senayan | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Simpul kerawanan #2 dan #6.
PKTGN | Petukangan | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | 1 GI. Feeder Petukangan-Senayan bermasalah (SKTT rusak); Senayan tetap disuplai dari Kembangan.
PSKBR | Pasar Kemis Baru | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Kerawanan #3 (Pasar Kemis Baru-Gajah Tunggal-Pasar Kemis single phi)
PSKMS | Pasar Kemis | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Irisan 2 SLD. Kerawanan #3 (single phi).
SDJYA | Sindang Jaya | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
SGS | Summarecon Gading Serpong | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
SNYAN | Senayan | GIS | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | GIS kawasan Zero Down Time (ZDT), disuplai radial dari SKTT New Senayan-Senayan. Kerawanan #6.
SPTAN | Sepatan | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
SPTAN2 | Sepatan 2 | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Dead-end load
SVRNA | Suvarna Sutra | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | Irisan 2 SLD
TGBRU | Tangerang Baru | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
TGBRU_3 | Tangerang Baru 3 | GI | 150 | UP2B Jakarta & Banten | JBB | NEW_NOT_ENERGIZED | UNKNOWN |  | 0 | 0 |  |  |  |  | Busbar hitam di SLD = belum energize
TGRNG | Tangerang | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | GI Tangerang (Lama). Bebannya akan diambil GITET Cikupa (RUPTL). Hotspot #5.
TLKGA | Teluknaga | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 1 | 1 shunt capacitor |  |  |  | GI Teluknaga (berbeda dari GI Lontar)
TLKNG2_DADAP | Teluknaga 2 / Dadap | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0
ULJMI | Ulujami | GI | 150 | UP2B Jakarta & Banten | JBB | ENERGIZED | UNKNOWN |  | 1 | 0 |  |  |  |  | GI terpisah dari Senayan; disuplai dari New Senayan. Dead-end load (trafo 150/20 saja).

## 02_TRANSFORMER
Code | Name | Type | Substation_Code | Unit_No | Rating_MVA | Winding_Count | Windings | Status | Asset_ID | Note
IBT_KMBGN_1 | IBT 1 Kembangan | IBT | KMBGN | 1 | 500 | 2 | 1:500.0kV(HV) ¦ 2:150.0kV(LV) | ENERGIZED
IBT_KMBGN_2 | IBT 2 Kembangan | IBT | KMBGN | 2 | 500 | 2 | 1:500.0kV(HV) ¦ 2:150.0kV(LV) | ENERGIZED
IBT_NBRJA_1 | IBT 1 New Balaraja | IBT | NBRJA | 1 | 500 | 2 | 1:500.0kV(HV) ¦ 2:150.0kV(LV) | ENERGIZED
IBT_NBRJA_2 | IBT 2 New Balaraja | IBT | NBRJA | 2 | 500 | 2 | 1:500.0kV(HV) ¦ 2:150.0kV(LV) | ENERGIZED

## 03_GENERATING_UNIT
Code | Name | Unit_Type | Voltage_kV | Rated_MW | Unit_Count | Outlet_Substation_Code | Operator | Status | Note
PLTU_LONTAR | PLTU Lontar | PLTU | 150 | 945 | 4 | LTKNG | PIP | ENERGIZED

## 04_CIRCUIT
Code | Name | Circuit_Type | Voltage_kV | From_Substation | To_Substation | Circuit_Count | Single_Phi | Status | Scenario | Confidence | Note
IBT_KMBGN_1_LINK | IBT 1 Kembangan 500/150 | IBT_LINK | 500 | GITET_KMBGN | KMBGN |  | 0 | ENERGIZED | NORMAL | 1
IBT_KMBGN_2_LINK | IBT 2 Kembangan 500/150 | IBT_LINK | 500 | GITET_KMBGN | KMBGN |  | 0 | ENERGIZED | NORMAL | 1
IBT_NBRJA_1_LINK | IBT 1 New Balaraja 500/150 | IBT_LINK | 500 | GITET_NBRJA | NBRJA |  | 0 | ENERGIZED | NORMAL | 1
IBT_NBRJA_2_LINK | IBT 2 New Balaraja 500/150 | IBT_LINK | 500 | GITET_NBRJA | NBRJA |  | 0 | ENERGIZED | NORMAL | 1
PHT_ABDGP_MPANG | Abadi Guna Papan - Mampang | SKTT | 150 | ABDGP | MPANG | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; SKTT baru 1000A (teks p91)
PHT_ALTRA_SGS | Alam Sutera - Summarecon Gading Serpong | SKTT | 150 | ALTRA | SGS | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_BLRJA_CKNDE | Balaraja - Cikande | SKTT | 150 | BLRJA | CKNDE | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; CKNDE boundary -> Cilegon
PHT_BLRJA_SVRNA | Balaraja - Suvarna Sutra | SKTT | 150 | BLRJA | SVRNA | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced (cross-routing di SLD)
PHT_CKBRU_BSH | Cikupa Baru - BSH | SKTT | 150 | CKBRU | BSH | 1 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; BSH milik KTT
PHT_CKUPA_PSKMS | Cikupa - Pasar Kemis | SKTT | 150 | CKUPA | PSKMS | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_CKUPA_SVRNA | Cikupa - Suvarna Sutra | SKTT | 150 | CKUPA | SVRNA | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; spur
PHT_CLDUG_ALTRA | Ciledug - Alam Sutera | SKTT | 150 | CLDUG | ALTRA | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_CNKNG_TGRNG | Cengkareng - Tangerang | SKTT | 150 | CNKNG | TGRNG | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; Hotspot #5
PHT_DNYSA_ABDGP | Danayasa - Abadi Guna Papan | SKTT | 150 | DNYSA | ABDGP | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; Ruas Mampang-AGP-Danayasa (teks p91)
PHT_JTAKE_JTKBR | Jatake - Jatake Baru | SKTT | 150 | JTAKE | JTKBR | 2 | 0 | ENERGIZED | NORMAL | 0.8 | NEEDS_REVIEW; Jatake T5 -> Jatake Baru T6 (sisi Kembangan)
PHT_JTAKE_MAXIM | Jatake - Maxim | SKTT | 150 | JTAKE | MAXIM | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_KMBGN_DKSBI | Kembangan - Durikosambi | SKTT | 150 | KMBGN | DKSBI | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; DKSBI boundary stub
PHT_KMBGN_MTLAN | Kembangan - Metland | SKTT | 150 | KMBGN | MTLAN | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_KMBGN_PKTGN | Kembangan - Petukangan | SKTT | 150 | KMBGN | PKTGN | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
PHT_LTKNG_SDJYA | Lontar - Sindang Jaya | SKTT | 150 | LTKNG | SDJYA | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_LTKNG_TGBRU | Lontar - Tangerang Baru | SKTT | 150 | LTKNG | TGBRU | 2 | 0 | ENERGIZED | NORMAL | 0.7 | NEEDS_REVIEW; Ruas Lontar-Tangerang Baru (disebut di kerawanan #4)
PHT_LTKNG_TGBRU3 | Lontar - Tangerang Baru 3 | SKTT | 150 | LTKNG | TGBRU_3 | 2 | 0 | NEW_NOT_ENERGIZED | NORMAL | 0.4 | NEEDS_REVIEW; TGBRU 3 belum energize
PHT_LTKNG_TLKNG2 | Lontar - Teluknaga 2 / Dadap | SKTT | 150 | LTKNG | TLKNG2_DADAP | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_NBRJA_BLRJA | New Balaraja - Balaraja | SKTT | 150 | NBRJA | BLRJA | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_NCKUPA_JTAKE | GITET New Cikupa - Jatake (rencana) | IBT_LINK | 500 | NCKUPA | JTAKE | 2 | 0 | NEW_NOT_ENERGIZED | NORMAL | 0.4 | NEEDS_REVIEW; Future: saat GITET New Cikupa COD, menyuntik di area Cikupa-Jatake. Belum energize.
PHT_NSYAN_CLDUG | New Senayan - Ciledug | SKTT | 150 | NSYAN | CLDUG | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_NSYAN_ULJMI | New Senayan - Ulujami | SKTT | 150 | NSYAN | ULJMI | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; Ulujami dead-end load
PHT_SDJYA_SVRNA | Sindang Jaya - Suvarna Sutra | SKTT | 150 | SDJYA | SVRNA | 2 | 0 | ENERGIZED | NORMAL | 0.4 | NEEDS_REVIEW; traced
PHT_SGS_CURUG | Summarecon Gading Serpong - Curug | SKTT | 150 | SGS | CURUG | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
PHT_SNYAN_ABDGP | Senayan - Abadi Guna Papan | SKTT | 150 | SNYAN | ABDGP | 1 | 0 | PLANNED | NORMAL | 0.4 | NEEDS_REVIEW; Abu di SLD = perencanaan
PHT_SNYAN_DNYSA | Senayan - Danayasa | SKTT | 150 | SNYAN | DNYSA | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; DNYSA boundary -> Gandul 2,4
PHT_SPTAN_PSKBR | Sepatan - Pasar Kemis Baru | SKTT | 150 | SPTAN | PSKBR | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
PHT_SPTAN_SPTAN2 | Sepatan - Sepatan 2 | SKTT | 150 | SPTAN | SPTAN2 | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; Sepatan 2 dead-end
PHT_SVRNA_CKUPA | Suvarna Sutra - Cikupa | SKTT | 150 | SVRNA | CKUPA | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced (irisan)
PHT_TGBRU_CKBRU | Tangerang Baru - Cikupa Baru | SKTT | 150 | TGBRU | CKBRU | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; traced
PHT_TGBRU_ITS | Tangerang Baru - KTT ITS | SKTT | 150 | TGBRU | ITS | 1 | 0 | ENERGIZED | NORMAL | 0.4 | NEEDS_REVIEW; KTT ITS external
PHT_TGRNG_JTAKE | Tangerang - Jatake | SKTT | 150 | TGRNG | JTAKE | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; Jatake sebagai output bay dari sisi Balaraja (label PDF blur 'ITAKE' = JTAKE)
PHT_TGRNG_JTKBR | Tangerang - Jatake Baru | SKTT | 150 | TGRNG | JTKBR | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
PHT_TLKGA_SPTAN | Teluknaga - Sepatan | SKTT | 150 | TLKGA | SPTAN | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
PHT_TLKNG2_TLKGA | Teluknaga 2 / Dadap - Teluknaga | SKTT | 150 | TLKNG2_DADAP | TLKGA | 2 | 0 | ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; traced
SKTT_KMBGN_NSYAN | Kembangan - New Senayan | SKTT | 150 | KMBGN | NSYAN | 1 | 0 | ENERGIZED | NORMAL | 1 | Kerawanan #2: pembebanan 72%, N-1 tak terpenuhi
SKTT_NSYAN_SNYAN | New Senayan - Senayan | SKTT | 150 | NSYAN | SNYAN | 1 | 0 | ENERGIZED | NORMAL | 1 | Kerawanan #6: GIS Senayan ZDT, radial
SKTT_PKTGN_SNYAN | Petukangan - Senayan | SKTT | 150 | PKTGN | SNYAN | 1 | 0 | DE_ENERGIZED | NORMAL | 0.5 | NEEDS_REVIEW; Kabel eksisting rusak (teks p8/p87)
SUTT_CKBRU_CNKNG | Cikupa Baru - Cengkareng | SKTT | 150 | CKBRU | CNKNG | 2 | 0 | ENERGIZED | NORMAL | 0.6 | NEEDS_REVIEW; terkait kerawanan #5
SUTT_CKUPA_JTAKE | Cikupa - Jatake | SKTT | 150 | CKUPA | JTAKE | 2 | 0 | ENERGIZED | NORMAL | 1 | Kerawanan #4: overload saat N-1-1/N-2 ruas Lontar-Tangerang Baru
SUTT_DKSBI_CNKNG | Durikosambi - Cengkareng | SKTT | 150 | DKSBI | CNKNG | 2 | 0 | ENERGIZED | NORMAL | 1 | Kerawanan #5: N-1 tak terpenuhi saat GI Jatake/Jatake Baru/Tangerang/Cengkareng dipasok SS Muarakarang
SUTT_GJTGL_PSKMS | Gajah Tunggal - Pasar Kemis | SKTT | 150 | GJTGL | PSKMS | 1 | 1 | ENERGIZED | NORMAL | 0.7 | NEEDS_REVIEW; Kerawanan #3: garis tipis semi-hilang di SLD, menutup loop single-phi
SUTT_PSKBR_GJTGL | Pasar Kemis Baru - Gajah Tunggal | SKTT | 150 | PSKBR | GJTGL | 1 | 1 | ENERGIZED | NORMAL | 1 | Kerawanan #3: single phi; KTT Gajah Tunggal padam saat N-1-1
SUTT_PSKMS_PSKBR | Pasar Kemis - Pasar Kemis Baru | SKTT | 150 | PSKMS | PSKBR | 1 | 1 | ENERGIZED | NORMAL | 1 | Kerawanan #3: single phi Pasar Kemis Baru-Gajah Tunggal-Pasar Kemis

## 05_SUBSYSTEM
Code | Name | APB | Source_Ref
SS_LBK | Lontar - Balaraja 1,2 - Kembangan 1,2 | UP2B Jakarta & Banten | Buku Kerawanan SJB 2026 Sec 2.5

## 06_SS_MEMBERSHIP
Subsystem | Node_Kind | Node_Code | Role | External_Subsystem | Display_Order
SS_LBK | SUBSTATION | GITET_KMBGN | SOURCE |  | 1
SS_LBK | SUBSTATION | GITET_NBRJA | SOURCE |  | 1
SS_LBK | SUBSTATION | KMBGN | SOURCE |  | 1
SS_LBK | SUBSTATION | NBRJA | SOURCE |  | 1
SS_LBK | SUBSTATION | LTKNG | SOURCE |  | 1
SS_LBK | SUBSTATION | DKSBI | BOUNDARY | SS Muarakarang 1,2 - Durikosambi 1 - KIT Muarakarang | 1
SS_LBK | SUBSTATION | PKTGN | CORE |  | 1
SS_LBK | SUBSTATION | MTLAN | CORE |  | 2
SS_LBK | SUBSTATION | NSYAN | CORE |  | 2
SS_LBK | SUBSTATION | BLRJA | CORE |  | 2
SS_LBK | SUBSTATION | SDJYA | CORE |  | 2
SS_LBK | SUBSTATION | TLKNG2_DADAP | CORE |  | 2
SS_LBK | SUBSTATION | TGBRU | CORE |  | 2
SS_LBK | SUBSTATION | TGBRU_3 | CORE |  | 2
SS_LBK | SUBSTATION | CKNDE | BOUNDARY | SS GU Cilegon - Cilegon Baru 1,2,3 - Labuan | 2
SS_LBK | SUBSTATION | CLDUG | CORE |  | 3
SS_LBK | SUBSTATION | SNYAN | CORE |  | 3
SS_LBK | SUBSTATION | ULJMI | CORE |  | 3
SS_LBK | SUBSTATION | SVRNA | CORE |  | 3
SS_LBK | SUBSTATION | TLKGA | CORE |  | 3
SS_LBK | SUBSTATION | CKBRU | CORE |  | 3
SS_LBK | SUBSTATION | ITS | EXTERNAL_CONTEXT |  | 3
SS_LBK | SUBSTATION | ALTRA | CORE |  | 4
SS_LBK | SUBSTATION | DNYSA | BOUNDARY | SS Gandul 2,4 | 4
SS_LBK | SUBSTATION | ABDGP | BOUNDARY | SS Gandul 2,4 | 4
SS_LBK | SUBSTATION | MPANG | BOUNDARY | SS Gandul 2,4 | 4
SS_LBK | SUBSTATION | CKUPA | CORE |  | 4
SS_LBK | SUBSTATION | NCKUPA | CORE |  | 4
SS_LBK | SUBSTATION | SPTAN | CORE |  | 4
SS_LBK | SUBSTATION | CNKNG | CORE |  | 4
SS_LBK | SUBSTATION | BSH | EXTERNAL_CONTEXT |  | 4
SS_LBK | SUBSTATION | SGS | CORE |  | 5
SS_LBK | SUBSTATION | CURUG | CORE |  | 5
SS_LBK | SUBSTATION | PSKMS | CORE |  | 5
SS_LBK | SUBSTATION | PSKBR | CORE |  | 5
SS_LBK | SUBSTATION | SPTAN2 | CORE |  | 5
SS_LBK | SUBSTATION | TGRNG | CORE |  | 5
SS_LBK | SUBSTATION | JTAKE | CORE |  | 5
SS_LBK | SUBSTATION | MAXIM | CORE |  | 6
SS_LBK | SUBSTATION | JTKBR | CORE |  | 6
SS_LBK | SUBSTATION | GJTGL | CORE |  | 6
SS_LBK | GENERATING_UNIT | 1 | SOURCE |  | 1
SS_LBK | TRANSFORMER | 1 | SOURCE_BOUNDARY |  | 1
SS_LBK | TRANSFORMER | 2 | SOURCE_BOUNDARY |  | 1
SS_LBK | TRANSFORMER | 3 | SOURCE_BOUNDARY |  | 1
SS_LBK | TRANSFORMER | 4 | SOURCE_BOUNDARY |  | 1

## 07_RISK
Risk_Key | Subsystem | Seq_No | UIT | Attach_Kind | Attach_Label | Title | Kondisi | Dampak | Mitigasi | Usulan_Solusi | Priority | Status
RISK-SS_LBK-01 | SS_LBK | 1 | JBB | TRANSFORMER | IBT_KMBGN_1 | Pembebanan IBT-1,2 Kembangan tidak memenuhi N-1 saat PLTU Lontar -1 unit | Pembebanan IBT-1,2 Kembangan tidak memenuhi kriteria N-1 saat PLTU Lontar tidak beroperasi 1 unit. | 1. Terjadi pemadaman jika terjadi gangguan N-1 pada salah satu IBT Kembangan. 2. Pemeliharaan IBT Kembangan hanya dilakukan saat hari Minggu. | 1. Sudah terpasang OLS IBT Kembangan tahap 1 sd 4 sebesar 908 MW (Buku DS 2025). 2. Rencana penambahan target OLS IBT Kembangan tahap 1 sd 4 total 1207 MW. 3. Pekerjaan dilaksanakan saat beban pembangkitan Lontar 4 unit maksimum atau saat beban rendah. 4. Pengalihan beban ke Sub Sistem Muarakarang atau Gandul 1,3-Durikosambi 2. | Jangka Pendek: (1) GITET Cikupa + 2 unit IBT 500/150 kV + outlet (RUPTL 2025-2034, COD 2025); (2) 2 unit IBT 500/150 kV Ext IBT 3,4 Durikosambi (COD 2026); (3) PLTSA Tangerang 45 MW (COD 2028). Jangka Panjang: BESS di GI Cikupa & GI Teluknaga masing-masing 100 MW (COD 2032). | High | OPEN
RISK-SS_LBK-02 | SS_LBK | 2 | JBB | CIRCUIT | SKTT_KMBGN_NSYAN | Pembebanan SKTT Kembangan-New Senayan 72% / tidak memenuhi N-1 | Pembebanan SKTT Kembangan-New Senayan mencapai 72% / tidak memenuhi kriteria N-1. | 1. Terjadi Overload apabila trip 1 sirkit di ruas SKTT 150 kV Kembangan-New Senayan. 2. Fleksibilitas operasi dan keandalan berkurang. | 1. Sudah terpasang OLS SKTT Kembangan-New Senayan dengan target 120 MW (Buku DS 2025). 2. Pemeliharaan dilaksanakan saat beban rendah. 3. Pengalihan beban GI Danayasa ke Sub Sistem Cawang 2,3-Depok 1. | Jangka Pendek: (1) Pembangunan SKTT 150 kV Petukangan-PLTD Senayan menjadi 2cct, 1000 A/sirkit (kabel eksisting rusak, RUPTL 2025-2034, COD 2027); (2) 2 Line bay di GIS PLTD Senayan agar SKTT Petukangan-PLTD Senayan bisa operasi 2 sirkit (COD 2027). | High | OPEN
RISK-SS_LBK-03 | SS_LBK | 3 | JBB | CIRCUIT | SUTT_PSKBR_GJTGL | Ruas Pasar Kemis Baru-Gajah Tunggal-Pasar Kemis masih single phi | Ruas Penghantar Pasar Kemis Baru-Gajah Tunggal-Pasar Kemis masih beroperasi single phi. | Berpotensi Padam pada KTT GI Gajah Tunggal saat terjadi N-1-1. | Pengaturan penjadwalan pemeliharaan penghantar. | Jangka Menengah: Usulan Double Phi pada ruas Pasar Kemis Baru-Gajah Tunggal-Pasar Kemis (diusulkan COD 2029). | Medium | OPEN
RISK-SS_LBK-04 | SS_LBK | 4 | JBB | CIRCUIT | SUTT_CKUPA_JTAKE | Ruas Cikupa-Jatake berpotensi overload saat N-1-1 / N-2 ruas Lontar-Tangerang Baru | Ruas Penghantar Cikupa-Jatake berpotensi overload saat terjadi kondisi N-1-1 atau N-2 pada ruas penghantar Lontar-Tangerang Baru. | Pemeliharaan ruas penghantar Lontar-Tangerang Baru hanya bisa dilakukan saat beban rendah. | 1. Pengaturan penjadwalan pemeliharaan penghantar. 2. Sudah terpasang OLS SUTT Jatake-Cikupa sebesar 240 MW (Buku DS 2025). 3. Rencana penambahan target OLS SUTT Jatake-Cikupa total 375 MW (Buku DS 2025). | Jangka Pendek: GITET Cikupa + 2 unit IBT 500/150 kV + outlet untuk mengambil beban GI Cikupa, GI Jatake Baru, GI Maxim dan GI Tangerang Lama (RUPTL 2025-2034, COD 2025). Jangka Panjang: BESS di GI Cikupa & GI Teluknaga masing-masing 100 MW (COD 2032). | High | OPEN
RISK-SS_LBK-05 | SS_LBK | 5 | JBB | CIRCUIT | SUTT_DKSBI_CNKNG | Ruas Durikosambi-Cengkareng tidak memenuhi N-1 saat pasok dari SS Muarakarang | Ruas Penghantar Durikosambi-Cengkareng tidak memenuhi kriteria N-1 saat GI Jatake, Jatake Baru, Tangerang dan Cengkareng dipasok dari Sub Sistem Muarakarang. | 1. Berpotensi adanya pemadaman saat terjadi kondisi N-1 pada ruas penghantar tersebut. 2. Fleksibilitas operasi Sub Sistem Lontar dan Sub Sistem Muarakarang berkurang. | Pengaturan penjadwalan pemeliharaan penghantar hanya bisa dilakukan saat PLTU Lontar beroperasi 4 unit dan saat GI Jatake, Jatake Baru, Tangerang dan Cengkareng dipasok Sub Sistem Lontar. | Jangka Pendek: GITET Cikupa + 2 unit IBT 500/150 kV + outlet untuk mengambil beban GI Cikupa, GI Jatake Baru, GI Maxim dan GI Tangerang Lama (RUPTL 2025-2034, COD 2025). Jangka Panjang: BESS di GI Cikupa & GI Teluknaga masing-masing 100 MW (COD 2032). | High | OPEN
RISK-SS_LBK-06 | SS_LBK | 6 | JBB | SUBSTATION | SNYAN | GIS 150 kV Senayan (ZDT) dipasok radial dari SKTT New Senayan-Senayan | GIS 150 kV Senayan masuk dalam kawasan Zero Down Time (ZDT) namun saat ini dipasok radial dari SKTT New Senayan-Senayan. | Apabila terjadi N-1-1 pada ruas SKTT Kembangan-New Senayan menyebabkan GIS 150 kV Senayan padam. | Pengalihan beban ke Sub Sistem Cawang 2,3-Depok 1 atau Sub Sistem Muarakarang 1,2-Durikosambi 1-KIT Muarakarang saat pemeliharaan SKTT Kembangan-New Senayan. | Jangka Pendek: (1) 2 Line bay di GIS PLTD Senayan agar SKTT Petukangan-PLTD Senayan bisa operasi 2 sirkit (COD 2027); (2) SKTT 150 kV Petukangan-PLTD Senayan menjadi 2cct, 1000 A/sirkit (kabel eksisting rusak, RUPTL 2025-2034, COD 2027). | High | OPEN

## 08_DEFENSE_SCHEME
Scheme_Key | Name | Type | Status | Scope | Target_MW | Target_MW_Planned | Stages | Reference | Note
DS_OLS_IBT_KMBGN | OLS IBT Kembangan | OLS | ACTIVE | LOCAL | 908 | 1207 | tahap 1 sd 4 | Buku DS 2025
DS_OLS_JTAKE_CKUPA | OLS SUTT Jatake-Cikupa | OLS | ACTIVE | LOCAL | 240 | 375 |  | Buku DS 2025
DS_OLS_KMBGN_NSYAN | OLS SKTT Kembangan-New Senayan | OLS | ACTIVE | LOCAL | 120 |  |  | Buku DS 2025

## 09_DS_RELATION
Scheme_Key | Subsystem | Attach_Kind | Attach_Label | Role | Coverage_Note
DS_OLS_IBT_KMBGN | SS_LBK | TRANSFORMER | IBT_KMBGN_1 | TRIGGER_ACTION | 1 SS
DS_OLS_IBT_KMBGN | SS_LBK | TRANSFORMER | IBT_KMBGN_2 | TRIGGER_ACTION | 1 SS
DS_OLS_KMBGN_NSYAN | SS_LBK | CIRCUIT | SKTT_KMBGN_NSYAN | TRIGGER_ACTION | 1 SS
DS_OLS_JTAKE_CKUPA | SS_LBK | CIRCUIT | SUTT_CKUPA_JTAKE | TRIGGER_ACTION | 1 SS

## 10_TOPOLOGY_VERSION
Version_Key | Status | Effective_Date | Reviewer | Approver | Description
TV-SS_LBK-2026-06 | ACTIVE | 2026-06-30 |  |  | Baseline SS Lontar-Balaraja-Kembangan dari Buku Kerawanan SJB 2026 Sec 2.5 (traced from SLD hal.69-70; edge confidence-tagged, pending field review).
TV-SS_LBK-NCKUPA-COD | PROPOSED |  |  |  | Saat GITET New Cikupa (IBT 500/150) COD: menjadi sumber Tier-1 baru yang menyuntik di area Cikupa-Jatake, menghilangkan overload ruas Cikupa-Jatake (kerawanan #4).

## 11_CHANGESET
Change_Key | Version | Action | Target_Kind | Target_Ref | Status | Description
CR-SS_LBK-001 | TV-SS_LBK-NCKUPA-COD | ADD_GITET | SUBSTATION | NCKUPA | PROPOSED | Energize GITET New Cikupa; ubah status PHT_NCKUPA_JTAKE -> ENERGIZED; evaluasi ulang beban ruas Cikupa-Jatake.